## Sheet1
Velocity Survey for Furnace Blower at 4 Speeds
Feburary 18, 2013
These velocity profiles were meaured on the Emerson 1/2 hp furnace fan bought at the Restore.
A rectangular exit duct 2 ft long and with a 1 sf exit area was attached to the blower exit -- but, velocity variation across the duct was still large -- thus the 75 point (fine) velocity survey.
Velocities were measured with the Alnor Velometer.
Sheets 1 through 4 have the velocities for each of the 4 speeds 1 is low and 4 is high.
The 5 velocity columins are marked by the holes near the top of the duct.
Fan on High Speed (4) with rectangular duct with 1 sf exit: | [8 empty] | The velocity was measure at 15 points for each column.
2/14/2013? |  | 1 | 2 | 3 | 4 | 5 |  |  | The Velometer pitot tube (picture) was used for the measurements.
| 1 | 4750 | 4800 | 4200 | 3800 | 4200
| 2 | 4050 | 3990 | 3450 | 3250 | 4150 |  |  | The reason that lots of (15) points were measured in each column is that the velocity varied
| 3 | 3440 | 3200 | 2920 | 2640 | 3720 |  |  | rapidly across the section -- especially near the duct walls.
| 4 | 2750 | 2780 | 2450 | 2320 | 3300
| 5 | 2190 | 2320 | 2250 | 2130 | 3050
| 6 | 1950 | 2110 | 2280 | 2050 | 2750
| 7 | 1700 | 2000 | 2280 | 1980 | 2350
| 8 | 1610 | 1950 | 2250 | 1820 | 2220 |  |  |  | Summary:
| 9 | 1600 | 2020 | 2280 | 1750 | 2020 |  |  |  | speed | Vavg | Airlfow
| 10 | 1650 | 2050 | 2360 | 1780 | 2020 |  |  |  | 1 | 1427 | 1427
| 11 | 1720 | 2100 | 2550 | 1850 | 2070 |  |  |  | 2 | 1650 | 1650
| 12 | 1890 | 2250 | 2600 | 1950 | 2170 |  |  |  | 3 | 1946 | 1946
| 13 | 2100 | 2460 | 2770 | 2160 | 2250 |  |  |  | 4 | 2540 | 2540
| 14 | 2250 | 2630 | 2950 | 2350 | 2200
| 15 | 2210 | 2730 | 3000 | 2250 | 2100 |  |  |  | Velocities in fpm, and flows in cfm
[6 empty] | Vavg | 2539.8667
Velocity distribution by column:
|  | Col1 |  |  |  |  | Col 2 | Col 3 |  |  |  | Col 4 | Col 5

## Sheet2
Fan on Med-Lo speed (2) with 1 sf exit duct -- 2/19/13:
| 1 | 2 | 3 | 4 | 5
| 2700 | 2700 | 2450 | 2700 | 2650
| 2600 | 2650 | 2250 | 2450 | 2650
| 2200 | 2000 | 2270 | 1920 | 2450
| 2050 | 1680 | 2070 | 1650 | 2250
| 1800 | 1500 | 1770 | 1520 | 1950
| 1750 | 1250 | 1700 | 1450 | 1780
| 1450 | 1120 | 1500 | 1300 | 1600
| 1280 | 1050 | 1450 | 1240 | 1500
| 1240 | 1080 | 1480 | 1140 | 1270
| 1070 | 1100 | 1520 | 1100 | 1270
| 1070 | 1150 | 1530 | 1220 | 1270
| 980 | 1250 | 1600 | 1420 | 1400
| 980 | 1430 | 1650 | 1500 | 1470
| 1000 | 1610 | 1940 | 1520 | 1650
| 920 | 1770 | 2000 | 1570 | 1300
[5 empty] | Vavg | 1650.2667

## Sheet3
Fan on Med-Hi (3) with 1 sf exit duct -- 2/19/13:
| 1 | 2 | 3 | 4 | 5
| 3700 | 3650 | 2800 | 3400 | 3400
| 3020 | 2980 | 2650 | 2650 | 3400
| 2980 | 2250 | 2500 | 2380 | 3050
| 2200 | 1950 | 1950 | 2100 | 2700
| 2150 | 1650 | 1840 | 1850 | 2400
| 1900 | 1450 | 1800 | 1680 | 2000
| 1620 | 1380 | 1860 | 1500 | 1850
| 1350 | 1390 | 1800 | 1450 | 1600
| 1400 | 1350 | 1780 | 1300 | 1450
| 1320 | 1500 | 1800 | 1300 | 1380
| 1160 | 1500 | 1950 | 1350 | 1450
| 1400 | 1580 | 1950 | 1580 | 1490
| 1200 | 1700 | 2060 | 1650 | 1650
| 1180 | 2020 | 2300 | 1700 | 1550
| 1000 | 2000 | 2420 | 1650 | 1700
[5 empty] | Vavg | 1946.6667

## Sheet4
Furnace Blower on low speed -- velocity survey with Velometer -- 2/16/13:
| Col 1 | Col 2 | Col 3 | Col 4 | Col5
| 2700 | 2700 | 1950 | 2380 | 2210
| 2270 | 2250 | 1770 | 1940 | 2150
| 1930 | 1920 | 1700 | 1750 | 2080
| 1610 | 1500 | 1400 | 1500 | 1840
| 1450 | 1300 | 1280 | 1280 | 1700
| 1280 | 1150 | 1140 | 1200 | 1570
| 1120 | 1050 | 1080 | 1150 | 1425
| 1000 | 1080 | 1070 | 1050 | 1450
| 1000 | 1020 | 1080 | 1020 | 1200
| 1040 | 1120 | 1140 | 1000 | 1100
| 1040 | 1200 | 1200 | 1000 | 1150
| 1020 | 1350 | 1320 | 1100 | 1250
| 1140 | 1450 | 1450 | 1170 | 1270
| 1360 | 1510 | 1550 | 1200 | 1460
| 1300 | 1520 | 1600 | 1010 | 1300
[6 empty] | Vavg | 1426.8667
| 1417.3333 | 1474.6667 | 1382 | 1316.6667 | 1543.6667
1426.8667